## Guideline Calculator
Safety Guideline for Indoor Airborne Transmission of COVID-19
Martin Z. Bazant
Contact: | bazant@mit.edu |  | http://www.mit.edu/~bazant
History: 6-4-2020 (v1), 7-1-2020 (v2), | 8-16 (v3), medRxiv 9-1-2020 (v4), 10-20 (v5), 1-20-2021 (v6)
This version: 4-12-2021 (v7 PNAS, with Alex E. Cohen)
For an online app, edX course other resources, please visit: |  |  | http://www.mit.edu/~bazant/COVID-19
References: 1. Martin Z. Bazant and John W. M. Bush, PNAS (2021).
"Beyond Six Feet: A Guideline to Limit Indoor Airborne Transmission of COVID-19"
Detailed instructions are in the Supporting Information, SI Appendix, Section 7.
2. M.Z. Bazant, O. Kodio, A. E. Cohen, K. Khan. Z. Gu & J. W. M. Bush, medRxiv (2021).
Monitoring carbon dioxide to quantify the risk of indoor airborne transmission of CO2.
Input values are in the pink cells.
Physical Parameters
Floor area, A | 910 | ft2 | 84.5418 | m2
Mean ceiling height, H | 12 | ft | 3.6576 | m
Room volume, V | 10920 | ft3 | 309.22 | m3
Outdoor air exchange rate, la | 3 | /hr (ACH)
Ventilation (outdoor air) flow rate, Q | 546 | ft3/min | 927.6599 | m3/hr
Recirculation air exchange rate, lr | 1 | /hr (ACH) | (includes HVAC & air filtration units)
Recirculation (return) flow rate, Qr | 182 | ft3/min | 309.22 | m3/hr
Primary (total) air flow rate, Q+Qr | 728 | ft3/min | 1236.8799 | m3/hr
Primary outdoor air fraction, Zp | 0.75 | (=1.0 natural ventilation, or no recirculation)
Aerosol filtration efficiency, pf | 0.01 | (>0.9997 HEPA, =0.2-0.9 MERVs, =0 no filter)
Air filtration rate, lf | 0.01 | /hr
Relative humidity, RH | 60 | %
Physiological Parameters
Mean breathing flow rate, Qb | 0.2884 | ft3/min | 0.49 | m3/hr (=0.5 rest, =1-3 active)
Respiratory aerosol radius, r | 2 | mm | (depends weakly on activity, disease)
Humidity-adjusted radius | 2 | mm
Disease Parameters
Infectiousness of exhaled air, Cq | 72 | infection quanta/m3 |  | (depends on activity, Fig. 2)
Viral deactivation rate, lv @ 50% RH | 0.3 | /hr | 3.3333 | hour deactivation time
Humidity-adjusted deactivation rate | 0.36 | /hr | (assume linear in RH)
Relative transmissibility, sr | 1 | (=0.23 for children, 0.68 for adults, 1.0 for elderly,
multiply by 1.6 for B.1.1.7 UK variant of concern)
Infectious Aerosol Properties |  |  | (1100 kg/m^3 density of droplet nuclei)
Effective settling speed, vs(r) | 0.51517 | mm/sec | 1.8546 | m/hr
Concentration relaxation rate, lc | 3.8771 | /hr | 0.25793 | hour relaxation time
Dilution factor, fd | 0.00040872 | infectiousness of ambient air / exhaled breath
Infectiousness of room air, fd Cq | 0.029428 | infection quanta/m3 in steady state
Precautionary Parameters
Mask aerosol passage probability, pm | 0.145 | (=1 no masks, 0.01-0.1 surgical, 0.1-0.4 hybrid fabric )
Airborne transmission rate, ba | 0.00030317 | /hr | (per pair of persons in steady state)
Risk tolerance, e | 0.1 | (bound on Rin, expected transmissions per infector)
To limit transmission, in the presence of one infected person (Rin < e):
Safe Room Occupancy
Exposure time, t | 10 | hours | (net before testing/removal/recovery)
Maximum safe occupancy, Nmax | 34 | persons | (with transient aerosol buildup)
| 33 | persons | (steady state aerosol concentration)
6 FOOT RULE (CDC) | 25 | persons
1 METER RULE (WHO) | 84 | persons
Minimum outdoor airflow / person | 15 | ft3/min | 7.0792 | L/s
Maximum occupancy for outdoor air | 36.4 | persons
Safe Exposure Time
Room occupancy, N | 25 | persons
Maximum exposure time, tmax | 13.9968 | hours | 839.8072 | minutes (transient)
| 13.7435 | hours | 824.6116 | minutes (steady state)
If carbon dioxide data is available:
Background CO2 concentration | 410 | ppm | (N=0 or outdoor ~250-450, rural to urban)
Average CO2 during occupancy time | 700 | ppm | (with exhaled CO2 > background)
Maximum exposure time, tmax | 22.8298 | hours | 1369.7887 | minutes (transient)
Given the exposure time:
Safe CO2 Concentration | 1072.0645 | ppm | (only to limit airborne transmission,
> 5000 ppm for 8 hours is unhealthy)

## Plot Data
t (hours) | N | Transient cumulative exposure time bound
0 | 10000 | epsilon | beta_a | lambda_c | N (6 ft rule) | 0.46656 | dtau
0.46656 | 1098.8065 | 0.1 | 0.00030317 | 3.8771 | 25
0.93312 | 452.1947 | 0.1 | 0.00030317 | 3.8771 | 25
1.3997 | 280.0834 | 0.1 | 0.00030317 | 3.8771 | 25
1.8662 | 202.1702 | 0.1 | 0.00030317 | 3.8771 | 25
2.3328 | 158.0278 | 0.1 | 0.00030317 | 3.8771 | 25
2.7994 | 129.6852 | 0.1 | 0.00030317 | 3.8771 | 25
3.2659 | 109.9722 | 0.1 | 0.00030317 | 3.8771 | 25
3.7325 | 95.4783 | 0.1 | 0.00030317 | 3.8771 | 25
4.199 | 84.3776 | 0.1 | 0.00030317 | 3.8771 | 25
4.6656 | 75.6056 | 0.1 | 0.00030317 | 3.8771 | 25
5.1322 | 68.5002 | 0.1 | 0.00030317 | 3.8771 | 25
5.5987 | 62.6285 | 0.1 | 0.00030317 | 3.8771 | 25
6.0653 | 57.6951 | 0.1 | 0.00030317 | 3.8771 | 25
6.5318 | 53.4921 | 0.1 | 0.00030317 | 3.8771 | 25
6.9984 | 49.8685 | 0.1 | 0.00030317 | 3.8771 | 25
7.465 | 46.7125 | 0.1 | 0.00030317 | 3.8771 | 25
7.9315 | 43.939 | 0.1 | 0.00030317 | 3.8771 | 25
8.3981 | 41.4825 | 0.1 | 0.00030317 | 3.8771 | 25
8.8646 | 39.2917 | 0.1 | 0.00030317 | 3.8771 | 25
9.3312 | 37.3257 | 0.1 | 0.00030317 | 3.8771 | 25
9.7978 | 35.5516 | 0.1 | 0.00030317 | 3.8771 | 25
10.2643 | 33.9426 | 0.1 | 0.00030317 | 3.8771 | 25
10.7309 | 32.4767 | 0.1 | 0.00030317 | 3.8771 | 25
11.1974 | 31.1357 | 0.1 | 0.00030317 | 3.8771 | 25
11.664 | 29.9042 | 0.1 | 0.00030317 | 3.8771 | 25
12.1305 | 28.7694 | 0.1 | 0.00030317 | 3.8771 | 25
12.5971 | 27.7203 | 0.1 | 0.00030317 | 3.8771 | 25
13.0637 | 26.7475 | 0.1 | 0.00030317 | 3.8771 | 25
13.5302 | 25.8431 | 0.1 | 0.00030317 | 3.8771 | 25
13.9968 | 25 | 0.1 | 0.00030317 | 3.8771 | 25
14.4633 | 24.2122 | 0.1 | 0.00030317 | 3.8771 | 25
14.9299 | 23.4746 | 0.1 | 0.00030317 | 3.8771 | 25
15.3965 | 22.7823 | 0.1 | 0.00030317 | 3.8771 | 25
15.863 | 22.1314 | 0.1 | 0.00030317 | 3.8771 | 25
16.3296 | 21.5183 | 0.1 | 0.00030317 | 3.8771 | 25
16.7961 | 20.9397 | 0.1 | 0.00030317 | 3.8771 | 25
17.2627 | 20.3928 | 0.1 | 0.00030317 | 3.8771 | 25
17.7293 | 19.8752 | 0.1 | 0.00030317 | 3.8771 | 25
18.1958 | 19.3845 | 0.1 | 0.00030317 | 3.8771 | 25
18.6624 | 18.9186 | 0.1 | 0.00030317 | 3.8771 | 25
19.1289 | 18.4757 | 0.1 | 0.00030317 | 3.8771 | 25
19.5955 | 18.0542 | 0.1 | 0.00030317 | 3.8771 | 25
20.0621 | 17.6526 | 0.1 | 0.00030317 | 3.8771 | 25
20.5286 | 17.2694 | 0.1 | 0.00030317 | 3.8771 | 25
20.9952 | 16.9035 | 0.1 | 0.00030317 | 3.8771 | 25
21.4617 | 16.5537 | 0.1 | 0.00030317 | 3.8771 | 25
21.9283 | 16.2189 | 0.1 | 0.00030317 | 3.8771 | 25
22.3949 | 15.8982 | 0.1 | 0.00030317 | 3.8771 | 25
22.8614 | 15.5908 | 0.1 | 0.00030317 | 3.8771 | 25
23.328 | 15.2958 | 0.1 | 0.00030317 | 3.8771 | 25
23.7945 | 15.0125 | 0.1 | 0.00030317 | 3.8771 | 25
24.2611 | 14.7402 | 0.1 | 0.00030317 | 3.8771 | 25
24.7277 | 14.4782 | 0.1 | 0.00030317 | 3.8771 | 25
25.1942 | 14.2261 | 0.1 | 0.00030317 | 3.8771 | 25
25.6608 | 13.9832 | 0.1 | 0.00030317 | 3.8771 | 25
26.1273 | 13.7491 | 0.1 | 0.00030317 | 3.8771 | 25
26.5939 | 13.5233 | 0.1 | 0.00030317 | 3.8771 | 25
27.0605 | 13.3054 | 0.1 | 0.00030317 | 3.8771 | 25
27.527 | 13.0949 | 0.1 | 0.00030317 | 3.8771 | 25
27.9936 | 12.8914 | 0.1 | 0.00030317 | 3.8771 | 25
28.4601 | 12.6947 | 0.1 | 0.00030317 | 3.8771 | 25
28.9267 | 12.5045 | 0.1 | 0.00030317 | 3.8771 | 25
29.3933 | 12.3203 | 0.1 | 0.00030317 | 3.8771 | 25
29.8598 | 12.1419 | 0.1 | 0.00030317 | 3.8771 | 25
30.3264 | 11.969 | 0.1 | 0.00030317 | 3.8771 | 25
30.7929 | 11.8014 | 0.1 | 0.00030317 | 3.8771 | 25
31.2595 | 11.6389 | 0.1 | 0.00030317 | 3.8771 | 25
31.726 | 11.4812 | 0.1 | 0.00030317 | 3.8771 | 25
32.1926 | 11.3281 | 0.1 | 0.00030317 | 3.8771 | 25
32.6592 | 11.1794 | 0.1 | 0.00030317 | 3.8771 | 25
33.1257 | 11.0349 | 0.1 | 0.00030317 | 3.8771 | 25
33.5923 | 10.8945 | 0.1 | 0.00030317 | 3.8771 | 25
34.0588 | 10.7579 | 0.1 | 0.00030317 | 3.8771 | 25
34.5254 | 10.6251 | 0.1 | 0.00030317 | 3.8771 | 25
34.992 | 10.4958 | 0.1 | 0.00030317 | 3.8771 | 25
35.4585 | 10.3699 | 0.1 | 0.00030317 | 3.8771 | 25
35.9251 | 10.2474 | 0.1 | 0.00030317 | 3.8771 | 25
36.3916 | 10.128 | 0.1 | 0.00030317 | 3.8771 | 25
36.8582 | 10.0116 | 0.1 | 0.00030317 | 3.8771 | 25
37.3248 | 9.8982 | 0.1 | 0.00030317 | 3.8771 | 25
37.7913 | 9.7876 | 0.1 | 0.00030317 | 3.8771 | 25
38.2579 | 9.6797 | 0.1 | 0.00030317 | 3.8771 | 25
38.7244 | 9.5745 | 0.1 | 0.00030317 | 3.8771 | 25
39.191 | 9.4717 | 0.1 | 0.00030317 | 3.8771 | 25
39.6576 | 9.3714 | 0.1 | 0.00030317 | 3.8771 | 25
40.1241 | 9.2735 | 0.1 | 0.00030317 | 3.8771 | 25
40.5907 | 9.1778 | 0.1 | 0.00030317 | 3.8771 | 25
41.0572 | 9.0842 | 0.1 | 0.00030317 | 3.8771 | 25
41.5238 | 8.9928 | 0.1 | 0.00030317 | 3.8771 | 25
41.9904 | 8.9035 | 0.1 | 0.00030317 | 3.8771 | 25
42.4569 | 8.8161 | 0.1 | 0.00030317 | 3.8771 | 25
42.9235 | 8.7307 | 0.1 | 0.00030317 | 3.8771 | 25
43.39 | 8.647 | 0.1 | 0.00030317 | 3.8771 | 25
43.8566 | 8.5652 | 0.1 | 0.00030317 | 3.8771 | 25
44.3232 | 8.4851 | 0.1 | 0.00030317 | 3.8771 | 25
44.7897 | 8.4067 | 0.1 | 0.00030317 | 3.8771 | 25
45.2563 | 8.3299 | 0.1 | 0.00030317 | 3.8771 | 25
45.7228 | 8.2547 | 0.1 | 0.00030317 | 3.8771 | 25
46.1894 | 8.181 | 0.1 | 0.00030317 | 3.8771 | 25
46.656 | 8.1088 | 0.1 | 0.00030317 | 3.8771 | 25
47.1225 | 8.038 | 0.1 | 0.00030317 | 3.8771 | 25
47.5891 | 7.9687 | 0.1 | 0.00030317 | 3.8771 | 25
48.0556 | 7.9006 | 0.1 | 0.00030317 | 3.8771 | 25
48.5222 | 7.8339 | 0.1 | 0.00030317 | 3.8771 | 25
48.9888 | 7.7685 | 0.1 | 0.00030317 | 3.8771 | 25
49.4553 | 7.7043 | 0.1 | 0.00030317 | 3.8771 | 25
49.9219 | 7.6414 | 0.1 | 0.00030317 | 3.8771 | 25
50.3884 | 7.5795 | 0.1 | 0.00030317 | 3.8771 | 25
50.855 | 7.5189 | 0.1 | 0.00030317 | 3.8771 | 25
51.3216 | 7.4593 | 0.1 | 0.00030317 | 3.8771 | 25
51.7881 | 7.4008 | 0.1 | 0.00030317 | 3.8771 | 25